## Vỏ
Cad: | N.H.Hoang | Product: 3750kVA PAD_MOUNTED TRANSFORMER 24.9/4.16
Check: | V.T.Binh | Tên bản vẽ/Description: | Số bản vẽ/Draw no:
Approve: | M.N.Trinh | TANK | Tỷ lệ/Scale:
#VALUE! |  |  | Số lượng (Quantity):
Note:

## TON2
Limb 1
Step | B | L1 | M1 | L2 | M2 | L3 | M3 | Thickness |  | Number of sheets |  | LIMB 2 | [9 empty] | YOKE | [8 empty] | Weight
[8 empty] | HV | LV | Total | Type 1-2-3 | Step | B | LT | C | C1 | HV |  | LV |  |  | Step | B | LX | C2 | C3 | HV |  | LV |  | (kg)
01 | 260 | 1045 | 1.5 | 1045 | 4.5 | 1045 | 7.5 | 52 | 52 | 434.1 | 145 | 01 | 260 | 1305 | 1045 | 785 | 52 | x2 | 52 | x2 |  | 01 | 260 | 1300 | 520 | 260 | 52 | x2 | 52 | x2 | 1044
02 | 250 | 1035 | 1.5 | 1035 | 4.5 | 1035 | 7.5 | 25 | 25 | 208.7 | 70 | 02 | 250 | 1285 | 1035 | 785 | 25 | x2 | 25 | x2 |  | 02 | 250 | 1290 | 520 | 270 | 25 | x2 | 25 | x2 | 479.8
03 | 240 | 1035 | 1.5 | 1035 | 4.5 | 1035 | 7.5 | 13.5 | 13.5 | 112.7 | 38 | 03 | 240 | 1275 | 1035 | 795 | 13.5 | x2 | 13.5 | x2 |  | 03 | 240 | 1280 | 520 | 280 | 13.5 | x2 | 13.5 | x2 | 247.3
04 | 220 | 1035 | 1.5 | 1035 | 4.5 | 1035 | 7.5 | 18.5 | 18.5 | 154.4 | 51 | 04 | 220 | 1255 | 1035 | 815 | 18.5 | x2 | 18.5 | x2 |  | 04 | 220 | 1260 | 520 | 300 | 18.5 | x2 | 18.5 | x2 | 307
05 | 200 | 1035 | 1.5 | 1035 | 4.5 | 1035 | 7.5 | 13.5 | 13.5 | 112.7 | 38 | 05 | 200 | 1235 | 1035 | 835 | 13.5 | x2 | 13.5 | x2 |  | 05 | 200 | 1240 | 520 | 320 | 13.5 | x2 | 13.5 | x2 | 201.3
06 | 170 | 1035 | 1.5 | 1035 | 4.5 | 1035 | 7.5 | 15 | 15 | 125.2 | 42 | 06 | 170 | 1205 | 1035 | 865 | 15 | x2 | 15 | x2 |  | 06 | 170 | 1210 | 520 | 350 | 15 | x2 | 15 | x2 | 186.7
07 | 140 | 1035 | 1.5 | 1035 | 4.5 | 1035 | 7.5 | 11 | 11 | 91.8 | 31 | 07 | 140 | 1175 | 1035 | 895 | 11 | x2 | 11 | x2 |  | 07 | 140 | 1180 | 520 | 380 | 11 | x2 | 11 | x2 | 110.7
08 | 110 | 1035 | 1.5 | 1035 | 4.5 | 1035 | 7.5 | 8 | 8 | 66.8 | 22 | 08 | 110 | 1145 | 1035 | 925 | 8 | x2 | 8 | x2 |  | 08 | 110 | 1150 | 520 | 410 | 8 | x2 | 8 | x2 | 62.1
09 | 90 | 1035 | 1.5 | 1035 | 4.5 | 1035 | 7.5 | 4 | 2 | 25 | 8 | 09 | 90 | 1125 | 1035 | 945 | 4 | x2 | 2 | x2 |  | 09 | 90 | 1130 | 520 | 430 | 4 | x2 | 2 | x2 | 18.8
10 | 60 | 1035 | 1.5 | 1035 | 4.5 | 1035 | 7.5 | 4.5 | 0 | 18.8 | 6 | 10 | 60 | 1095 | 1035 | 975 | 4.5 | x2 | 0 | x2 |  | 10 | 60 | 1100 | 520 | 460 | 4.5 | x2 | 0 | x2 | 9.2
[29 empty] | Total weight = |  | 2667
CORE PARAMETERS
[17 empty] | Window height |  |  | 785 | (mm) | Distance between limb centers |  |  | 520 | (mm) | k= | 3 | i= | 5 | 7.5
[17 empty] | Net weight |  |  | 0 | (kg) | Gross weight |  |  | 0 | (kg) | kc= | 0.96 | Lamination type |  | 0.23
[14 empty] | Cad: N.H.Hoang | [9 empty] | Product: MBA 3750KVA 24.9±2x2.5%/4.16KV
0.00 | [13 empty] | Check: V.T.Binh | [9 empty] | Tên bản vẽ/Description: | [7 empty] | Draw no:
- Độ bavia ≤ 0,02 mm | [13 empty] | Approve: M.N.Trinh | [9 empty] | Core cutting | [7 empty] | Quantity:
- Try to cut 1 or 2 laminations, then inspect to ensure they meet requirements before proceeding with batch cutting | [13 empty] | #VALUE! | [17 empty] | Weight:
[24 empty] | Note: | [7 empty] | Scale:

## TON
Cad: | N.H.Hoang | Product: 3750kVA PAD_MOUNTED TRANSFORMER 24.9/4.16
Check: | V.T.Binh | Tên bản vẽ/Description: | Số bản vẽ/Draw no:
Approve: | M.N.Trinh | CORE | Tỷ lệ/Scale:
#VALUE! |  |  | Số lượng (Quantity):
Note:

## RUỘT
1. Clamp foot
2. Phase barrier
3. Neutral busbar
4. Yoke insulation
5. Core
6. Winding
7. Phase busbar
8. Core clamp assembly
Cad: | N.H.Hoang | Product: 3750kVA PAD_MOUNTED TRANSFORMER 24.9/4.16
Check: | V.T.Binh | Tên bản vẽ/Description: | Số bản vẽ/Draw no:
Approve: | M.N.Trinh | ACTIVE PART | Tỷ lệ/Scale:
#VALUE! |  |  | Số lượng (Quantity):
Note:

## pc_trụ giữa2
Cad: | N.H.Hoang | Product: 3750kVA PAD_MOUNTED TRANSFORMER 24.9/4.16
Check: | V.T.Binh | Tên bản vẽ/Description: | Số bản vẽ/Draw no:
Approve: | M.N.Trinh | CORE | Tỷ lệ/Scale:
#VALUE! |  |  | Số lượng (Quantity):
Note:

## pc_Móc cẩu1
Cad: | N.H.Hoang | Product: 3750kVA PAD_MOUNTED TRANSFORMER 24.9/4.16
Check: | V.T.Binh | Tên bản vẽ/Description: | Số bản vẽ/Draw no:
Approve: | M.N.Trinh | LIFTING LUG | Tỷ lệ/Scale:
#VALUE! |  |  | Số lượng (Quantity):
Note:

## pc_bản vẽ dây quấn 22KV
HV-LV distance: 9 = (2x0.13) DDP + 5.13mm spacer + 2(2x0.13) DDP + 1.5mm board + 2(2x0.13) DDP + flared collar + 0.5mm board + 2(2x0.13) DDP
HV-LV distance at outer LV copper busbar: 6 mm = 2 mm phase shielding board at wire end + 3 mm overlapping HV-LV board + (8x0.13) DDP
|  |  |  | 21 | Output wire lead size | 150
|  |  |  | 20 | Winding direction | Right | Left
|  |  |  | 19 | Spacers at both ends | 20 | 12
|  |  |  | 18 | Spacer in the middle coil | - | 12+11+12
|  |  |  | 17 | Coil height | 759 | 759
|  |  |  | 16 | Outer circumference of coil | 1806 | 1420
|  |  |  | 15 | Inner circumference of coil | 1479 | 973
|  |  |  | 14 | Mold circumference | 965
|  |  |  | 13 | Cooling duct size | 5.13 x 759 | 5.13 x 759
|  |  |  | 12 | Layers with cooling ducts | 6-7(HV-LV) 12-13(HV-LV) | 13-14(HV-LV) 22-23(HV-LV)
|  |  |  | 11 | Number of cooling ducts | 2 | 2
|  |  |  | 10 | Layer insulation | Xem chú thích | 2x0,13 | DDP
|  |  |  | 9 | Regulating turns | 20 | -
|  |  |  | 8 | Turns/layer | 49 | 1
|  |  |  | 7 | Total number of turns | 829 | 38+38
|  |  |  | 6 | Total number of layers | 18 | 38
|  |  |  | 5 | DC Resistance at 20 °C | 1.242085Ω | 0.00141Ω
NOTES: |  |  |  | 4 | Winding type | Cylindrical | Cylindrical
- Do not place LV cooling duct on the side with the copper busbar |  |  |  | 3 | Weight | 306.3 | 346.6
- Splint 15mm between ends 1 and 2 |  |  |  | 2 | Number of strands (stacked x arranged) | 1x2 | 1x2
- Make crepe paper flared collar 2x0.8 for HV (entire HV splint section) |  |  |  | 1 | Wire size | Al2 2x7 Enameled (2.12x7.12) | Al (1.3x350)x1x2
- After finishing HV, wrap 2 layers of DDP tightly around the coil |  |  |  | No. | Item | HV | LV
- HV shielding board place 3 sheets of 0.5mm. The rest are inserted after winding | Cad: | N.H.Hoang |  |  | Product: MBA 3750kVA 24.9/4.16 kV
- HV: apply glue to the first layer, the layer behind the cooling duct, and the regulating section | Check: | V.T.Binh |  |  | Tên bản vẽ/Description: |  | Số bản vẽ/Draw no:
- Outputs of HV-LV spacer tubes must be arranged evenly. | Approve: | M.N.Trinh |  |  | WINDING |  | Tỷ lệ/Scale:
- Layer insulation: Strip insulation (start 2 end 2) + Stepped insulation 759x(2x0.075)DDP + 506x0.18DDP + 253x0.05DDP | #VALUE! | [5 empty] | Số lượng (Quantity):
- Reinforce layer insulation: 759x0.18DDP + 570x0.18DDP + 380x0.18DDP + 190x0.18DDP at layer 1-2, last layer, and regulating section |  |  |  |  | Note: |  | Weight:

## NH
1. HV busing
2. HV parking stand
3. Load break switch
4. Tap changer
5. Bay-O-net fuse
6. Oil drip shield
7. Oil upper filling valve
8. Pressure relief device with contact
9. Vacuum pressure gauge with contact
10. Oil temperature indicator with contact
11. Oil level indicator with contact
12. Terminal box
13. LV-HV compartment
14, LV bushing intergrated
15. Name plate
16. Neutral bushing
17. Lower filtering valve with sampler
18. Radiator
19. Lifting lugs
[6 empty] | DIMENSIONS (mm) |  |  |  | WEIGHTS (kg)
[6 empty] | A | B | C | D | OIL | CORE&FOIL | TOTAL
[6 empty] | 2730 | 2200 | 2350 | 1700 | 3000 | 3740 | 8200
[6 empty] | ± 2% |  |  |  | ± 2%
TECHNICAL DATE
WINDING MATERIAL | AL | NOMINAL POWER [KVA] | 3750
FREQUENCY (Hz) | 60 | PRIMARY VOLTAGE [KV] | 24.9±2.5% DELTA | Cad: | N.H.Hoang |  |  | Product: 3750kVA PAD_MOUNTED TRANSFORMER 24.9/4.16
NO LOAD LOSSES (W) |  | SECONDARY VOLTAGE [KV] | 4.16 GRDY/2.4 | Check: | V.T.Binh |  |  | Tên bản vẽ/Description: |  |  | Số bản vẽ/Draw no:
LOAD LOSSES 85°C (W) |  | VECTOR GROUP | Dyn1 | Approve: | M.N.Trinh |  |  | OUTLINE |  |  | Tỷ lệ/Scale:
SHORT CIRCUI IPM [%] | 5.3 | FINAL COLOUR | Ral 7045 | #VALUE! | [6 empty] | Số lượng (Quantity):
ALTITUDE [m] | ≥ 1000 | LIQUID | Mineral oil | [7 empty] | Note: